## Slide 1
EYEWASH AND SAFETY SHOWER CHILLER
ASSURES SAFETY
REMOVES RISK
http://www.eyewashdirect.com/Haws-Eyewash-Safety-Shower-Eye-Wash-s
Notes: GOOD AFTERNOON LADIES AND GENTLEMEN
EMERGENCY EYEWASH SAFETY SHOWERS ARE PROVIDED AT JOBSITES TO PREVENT OR REDUCE INJURY CAUSED WHEN A WORKER IS EXPOSED TO A HARMFUL SUBSTANCE.
IN REMOTE HOT ENVIRONMENTS THE VAST MAJORITY OF THESE EYEWASH SAFETY SHOWERS ARE UNSAFE TO USE AND ARE LIKELY TO DO MORE HARM THAN GOOD

## Slide 2: p
An Introduction to Eyewash Safety Shower Legionella
An operator in the Northwest asked Heat Trap Solar for assistance with their eyewash safety showers
The client was concerned potable water supply temperatures could reach as high as 47oC in summer giving rise to the following issues:
Potable water supply temperatures above 37.8oC could lead to high risk water borne bacteria counts
Exposed stagnant potable water supply temperatures can reach >55oC which could result in scalding
High probability of excessive potable water losses in summer from anti-scald valves which are fully open at 39oC
Notes: In October 2013 a local contracting company contacted Heat Trap for some technical advice on chillers and for assistance in scoping a series of ringmain system to provide tepid water for emergency safety showers.
The client was concerned they may experience difficulties with excess water temperature causing loss of potable water from anti scald valves.

## Slide 3
THE PROBLEM
Notes: This cartoon illustrates the recognised issues for industries operating with potentially harmful contaminants in hot environments.
High ambient temperatures and exposed, stagnant potable water pipes lead to dangerously high water temperatures, high bacteria levels and uncontrolled loss of valuable potable water from anti-scald valve located at eyewash safety showers

## Slide 4: p
Heat Trap Solar Resolved the situation as follows
Heat Trap Solar designed, manufactured and installed stand-alone chillers which store up to 900L of water at 5oC
In use the stored chilled water is mixed with the incoming hot water to provide “tepid” water at the eyewash safety shower
The chiller continuously recirculates the water in the eyewash safety shower deadleg through a cooling coil and a UV sterilizer
Once a week the chiller automatically dumps the water from potable main to chiller to flush the line and to introduce fresh potable water which contains residual chlorine

## Slide 5: p
Benefits
The benefits that have been realised by the client through the installation of the HTS chiller units include:
Complete elimination of high water temperatures at Eyewash Safety Showers
95% reduction in the concentration of water borne bacteria to well below safe risk levels
Significant reduction in summer water usage at operating sites, saving >4 M Litres of potable water per annum
Reduction of water sampling requirements at Eyewash Safety Showers
Removal of water storage tanks and standardised the installation of Eyewash Safety Shower water supplies.
Notes: The benefits the Heat Trap chillers provide are:

## Slide 6: p
Before After
Notes: Previous unsuccessful attempt to overcome issues associated with excessive heat included above and below ground insulated water storage tanks.
The tanks instead became breeding grounds for bacteria because they stored water at temperatures above 20oC and were seldom, if ever, flushed sufficiently well enough to remove bacteria biofilms inside the tank.

## Slide 7
EYEWASH AND SAFETY SHOWER CHILLER
THE SOLUTION
Notes: The Heat Trap Chiller provides cooled flushing water, eliminates 95% of water borne bacteria and eliminates loss of potable water from the anti scald valves.
The chillers also provide assurance to management that the emergency eyewash safety showers remain safe to use all year round.

## Slide 8: p
ANCIENT ROMAN PROVERB
"In vino veritas, in aqua sanitas",
Pliny the Elder
"In wine there is truth, in water there is health."
Notes: This is a well known proverb from the past

## Slide 9: p
ANCIENT ROMAN PROVERB
"In vino veritas, in aqua sanitas",
Pliny the Elder
"In wine there is truth, in water there is health."
Benjamin Franklin is quoted as saying
“In Wine there is wisdom
In beer there is freedom
In water there is BACTERIA”
Notes: However it is very evident that industry operators have not heeded the warning as quoted by Benjamin Franklin.
I would now like to provide you with some interesting insight to water borne bacteria from the perspective of emergency eyewash safety showers

## Slide 10: p
A main Vector for Contracting Legionellosis is
Inhalation
  Inhalation of aerosol mists, fine sprays, or other microscopic droplets of water contaminated with Legionella - providing direct access into the lungs
Safety eyebaths, face washes and deluge showers all involve movement of water in air and all will generate aerosols
Notes: The means of contracting the Legionella disease are well understood.

## Slide 11: p
The risk of contracting Legionellosis is directly related to:
Status of the exposed person’s immune system
Duration of the exposure
Distance from the source of the contamination.
Amount of bacterial concentration in the water cfu/ml
Density of aerosolized water (respirable droplets) in the air being inhaled.
With eyewash safety showers we can’t influence the first three points but we can influence the effect of the last two.
Notes: What is also well known are the factors which influence the likelihood of a person contracting the disease.
They are:
Eyewash safety showers are a recognised agent for spreading the Legionella disease and it is worthwhile to examine some of the physical aspects of the design and operation of emergency eyewash safety showers to see how these parameters may add to the risk of contracting the disease.

## Slide 12: p
Water must be potable
Recommended maximum water temperature 37.8oC
Recommended minimum water temperature 15.6oC
Deluge flow rate >75.7 L/min for > 15 minutes
Facewash flow rate >11.6 L/min for > 15 minutes
Eyewash flow rate >1.5 L/min for > 15 minutes
(Standard domestic shower flow rates are 5.5 to 9 L/min)
AS4775 EYEBATH AND SAFETY SHOWER STANDARD
Notes: The Australian Standard AS4775 is modelled off the American Standard ANSI Z358 and specifies that the flushing water shall be potable and at a temperature which is safe to use.
Unfortunately this is often not the case.
The standard is designed around using potable water to flush away, dissolve and or dilute the corrosive substance affecting the patient.
The recommended upper temperature limit is set at 37.8oC as temperatures above this can cause damage to eyes and skin and may exacerbate the corrosive action of the substance.

## Slide 13: p
Notes: This is what the operator is subjected to.
The eyewash floods the eyes and the run off covers the nose and mouth in the process.
Similarly with the face wash only now the flow rate is increased from 1.5L/min to 11.4 L/min and the whole face is covered so that all air is inhaled through the flushing water.
Then there is the deluge shower.
The shower head is specifically designed to pour all 75.7 L/min in a tight circle with a maximum diameter of 508mm. Normal shower dispensed 9 L/min with a wider dispense angle.
Breathing under an emergency safety shower deluge is a very challenging experience.
So how much water is inhaled if you remain under the deluge for the full fifteen minutes.

## Slide 14: p
ANSI and Australian/NZ Standards safety shower standards both recommend large flow rates from the deluge shower in order to dissolve, dilute and physically drive off the contaminating substances from the body.
The high flow rates can give rise to a very high concentration of aerosolized water droplets in the air within the perimeter of the falling water.
AS 4775 minimum flow rate of 75 L/min is 8 X the flow rate from a standard shower.
Consider the concentration of aerosolised water in the air being inhaled when using an eye bath and/or deluge shower.
Notes: What I would like to discuss first is the amount of water dispensed from an eyewash safety shower and the way it is dispensed.
In particular I want to focus on what it is like to stand under am emergency safety shower pouring out 76 L/minute directly onto the top of your head. This is 8 times the flow rate from a normal shower and it is delivered at a minimum pressure of 210kPa.
Believe me this is a lot of water.
And you are required to stay under the shower for a minimum of 15 minutes.
In fact some mine sites require the operator to remain under the shower for a minimum of twenty minutes to allow sufficient time for the emergency response team to get to the site.

## Slide 15: p
TWO WAYS SAFETY SHOWERS CAN BE MADE SAFER
Lowering the temperature of the water to significantly reduce the amount of aerosols produced by the eyewash safety shower in operation.
Regular flushing with turbulent flow rates and reducing the hydraulic shock when the device opens can reduce the amount of bacteria sloughed off the fringes of the biofilm within the pipework.
Notes: Testing for legionella can be an expensive operation.
Every safety shower provides a unique set of circumstances for the accumulation of the legionella bacteria and each should be tested individually.
Full quantitative testing for legionella is generally performed in remote bio testing laboratories and collecting, delivering and testing samples from each and every eyewash safety shower on a regular basis can be extremely expensive.
Most processing plants which have eyewash safety showers installed also have procedures for the care, maintenance and regular servicing of them however only a very few regularly take samples for testing from each and every safety shower on the site.

## Slide 16: p
Graph data extrapolated from US NIH publication
Ref:
Zhou, Benson, Irvin, Irshad and Cheng
Particle Size Distribution and Inhalation Dose of Shower Water Under Selected Operating Conditions with flow rates of
5.1, 6.6 and 9.0 L/min
Lovelace Respiratory Research Institute 2007
Chart: 
| 5.0999999999999996 | 6.6 | 9 | 75
Hot Water 38oC | 11.26 | 11.98 | 14.21
Cold Water 25oC | 0.15 | 0.29 | 0.44
Projected Hot water 38oC | 14.21 | 50
Projected Cold water 25oC | 0.44 | 5.1
Between 5.1 and 9.0 L./min the inhaled hot water at 38oC is 30 – 70 X greater than cold water inhaled at 25oC
The amount of water particles inhaled can be significantly reduced simply by lowering the water temperature
WATER INHALED UNDER A HOT SHOWER IS 30+ TIMES MORE THAN IS INHALED UNDER A COLD SHOWER
Notes: Data on this topic is very limited however there was a study conducted by a group at the Lovelace Respiratory Research Institute which provides some very valuable insight.
The group tested three different shower heads with 5.1, 6.6 and 9 L/min flow rates and measured the amount of water which would be inhaled by a person standing under the shower for 10 minutes.
The first finding was that the larger the flow rate, the greater the amount of aerosols that were produced and inhaled.
This allows us to postulate that the amount of water particles inhales under a deluge of 75.7 L/min will be significantly larger than the amount of water particles inhaled under a standard 9 L/min shower.
What was of more interest was the finding that water temperature had a much more marked affect on the amount of water particles inhaled.
The difference between 25oC and 38oC is significant.
With a flow rate of 5.1 L/min there was 70 times more water particles inhaled under the hot shower than there was under the cold shower.
At 9 L/min flow rate the amount of water inhaled from a hot shower was 30 times more than was inhaled from a cold shower.
I understand there are standard thermodynamic and pyschrometric principles which explain this phenomena.
Similarly, humidity also plays a part and the higher the humidity the higher the percentage of very small water aerosol produced.
I low humidity environments, the very small water droplets evaporate before being inhaled.
IN SUMMARY
We can significantly reduce the amount of water aerosol particles inhaled whilst using an eyewash safety shower by simply lowering the temperature of the flushing fluid.

## Slide 17: p
Notes: Bringing the water temperature down from 38oC or above to 25oC will significantly reduce the amount of water that is inhaled when breathing unaided under a safety shower be it the eyebath, facewash or deluge shower.

## Slide 18: BIOFILM STABILITY CAN BE COMPROMISED WHEN HYDRAULIC SHOCK IS FOLLOWED BY TURBULENT FLOW RESULTING IN SLOUGHING OF FRINGE AREAS OF THE BIOFILM AND THE MASS RELEASE OF BACTERIA ORGANISMS
Notes: I would now like to speak briefly about pipe diameters and flow rates.
The standard AS4775 is silent on the matter of the diameter of pipework used to bring the flushing water from the potable main to the safety shower.
It is well known that flushing on its own will not entirely remove bacteria and biofilm from inside the pipe.
We do know that turbulent flow is superior to laminar flow in cleaning the inside of the pipe so lets look at some hydraulic parameters.
Turbulence occurs in a pipe when the physical parameters of viscosity, pipe diameter and flow rate are such that the combination o these factors produces a Reynolds number in excess of 4,000.
You can see from the above table that at low flow of 1.5 L/min there is turbulent flow only in the 15NB pipe.
At the higher flow rates associated with the facewash, deluge and combination of facewash and deluge that there is always turbulent flow in the pipework providing flushing water to the shower unit.
This is both good and bad.
It is good for removing the bacteria within the pipe and scouring the biofilm on the inside surface of the pipe.
There is a downside however if the pipes have not been flushed on a regular basis and the water left stagnant for a substantial length of time in temperatures conducive to rapid bacteria growth.
In these circumstances the bulk of the biofilm may not be tightly bound to the surface of the pipe.
The hydraulic shock and subsequent turbulent flow which occurs when the safety shower device is activated, can slough off the loosely held bacteria on the fringe of the biofilm and deliver this bulk release of bacteria as a slug to the dispensing device.

## Slide 19
TIME TAKEN TO FLUSH SUPPLY DEADLEGS OF VARIOUS DIAM AND FLOW RATES
Notes: Time is of the essence with eyewash safety showers and the Australian standard specifies quick acting valves, slam open and slam shut.
On most mine sites the static water pressure in the potable main is between 550kPa and 650 kPa and this is the pressure of the water within the biofilm.
When the shower unit is operated there is a rapid reduction in pressure followed by an acceleration of water flow within the pipe which can slough off the loosely held fringe portions of the biofilm and deliver the ultra high concentration of bacteria to the safety shower.
If we assume all the free and dislodged bacteria is removed to the shower by the incoming water then we can expect the danger period is the time it takes to replace the water in the delivery pipe.
As can be seen above, low flows and larger bore pipes can mean high does of bacteria can be delivered over substantial periods of time.
IN SUMMARY
Careful consideration on the diameter of the supply piping should be taken into account when sizing the pipework supplying the safety shower.
The effective length and the diameter of the line sets the expected pressure drop from the potable main to the shower and the smallest diameter which will deliver the required pressure at the shower should be specified.
More importantly there should be regular high flow flushing of the line to avoid the possibility of delivering very high doses of bacteria to the operator in the vital first minutes of operation.

## Slide 20: p
BENEFITS PROVIDED BY THE HTS CHILLER
The Heat Trap Chiller has achieved 95% reductions in water borne bacteria counts to well below safe risk levels.
The chiller lowers the temperature of the dispensed water reducing the number of aerosols generated.
The water used to mix with the incoming hot potable water is stored in the chiller at 5oC
The water in the deadleg between the chiller and the safety unit is continuously recirculated through a cooling coil and a UV sterilizer.
The chiller automatically dumps the water in the deadleg between the potable main and the chiller on a regular basis thereby flushing the line and bringing in fresh chlorinated water which contains residual chlorine.
Notes: Re-capping

## Slide 21: p
IN SUMMARY THE HEAT TRAP EYEWASH SAFETY SHOWER CHILLER ACHIEVES ALL OF THE FOLLOWING
Complete elimination of high water temperatures at Eyewash Safety Showers
95% reduction in the concentration of water borne bacteria to well below safe risk levels
Significant reduction in summer water usage at operating sites
Significant reduction of water sampling requirements at Eyewash Safety Showers
Provides management with the assurance the workers are not at risk because the eyewash safety showers are safe to use all year round
Notes: Testing for legionella can be an expensive operation.
Every safety shower provides a unique set of circumstances for the accumulation of the legionella bacteria and each should be tested individually.
Full quantitative testing for legionella is generally performed in remote bio testing laboratories and collecting, delivering and testing samples from each and every eyewash safety shower on a regular basis can be extremely expensive.
Most processing plants which have eyewash safety showers installed also have procedures for the care, maintenance and regular servicing of them however only a very few regularly take samples for testing from each and every safety shower on the site.

## Slide 22
EYEWASH AND SAFETY SHOWER CHILLER
THE SOLUTION
Notes: The Heat Trap Chiller provides cooled flushing water, eliminates 95% of water borne bacteria and eliminates loss of potable water from the anti scald valves.
The chillers also provide assurance to management that the emergency eyewash safety showers remain safe to use all year round.

## Slide 23
NATIONAL SAFETY COUNCIL OF AUSTRALIA
EXCELLENCE AWARDS OCTOBER 2016
RECEIVING
“HIGHLY COMMENDED”
AWARD
Notes: HEAT TRAP RECEIVED A ‘HIGHLY COMMENDED” AWARD AT THE NATIONAL SAFETY COUNCIL OF AUSTRALIA EXCELLENCE AWARDS HELD HERE IN SYDNEY IN OCTOBER.
THE SAFETY CREDIT SHOULD REALLY GO TO RIO TINTO FOR BEING THE FIRST COMPANY TO GO THAT ONE STEP FURTHER TO MAKE THEIR WORK PLACES SAFE AND FOR SUPPORTING THE LOCAL AUSTRALIAN MANUFACTURING INDUSTRY.